## Slide 1: SimPowerSystems Hands-on Workshop: Modeling and Simulation of Electrical Power Systems with SimPowerSystemsTM
Carlos Osorio
Principal Application Engineer
MathWorks – Natick, MA
7. Power Electronics

## Slide 2: Outline
SimElectronics or SimPowerSystems?
Ideal switching algorithm
Power quality and harmonic analysis
Control design and linearization

## Slide 3: SimElectronics or SimPowerSystems?
SimElectronics
Simultaneous nonlinear equations solution
SPICE level switching device models
Include switching losses
Include parasitic current effects
Include temperature effects
Higher fidelity simulation
SimPowerSystems
Piecewise linear systems solution
Multiphase bridges and pulse generators
Detailed and average voltage models
Transient and harmonic analysis
Faster simulation
>> se_dcdcbuckconverter
>> sps_dcdcbuckconverter

## Slide 4: SimElectronics or SimPowerSystems?
SimPowerSystems
SimElectronics

## Slide 5: SimElectronics or SimPowerSystems?
>> edit compare_powersupply
SimPowerSystems
SimElectronics

## Slide 6: Ideal switching algorithm
>> edit compare_idealswitching
  The ideal switching method can be selected from the solver configuration parameters tab when in Continuous simulation mode

## Slide 7: Ideal switching algorithm Effect of using snubber circuits
>> edit compare_snubbers
  Snubbers provide an alternate path for discharging inductive elements and protecting switching devices in high power systems

## Slide 8: Power quality and harmonic analysis Multi-pulse rectification
powergui
>> rectifier_6n12pulse
>> rectifier_24pulse

## Slide 9: Power quality and harmonic analysis Transformer rectifier units (TRUs)
>> transformer_rectifier_unit

## Slide 10: Power quality and harmonic analysis Switching strategies – Pulse-Width Modulation (PWM)
The aim of PWM is to construct a high frequency carrier wave which contains an underlying, lower frequency modulation wave
The modulation wave is the waveform that you want the electrical system to ‘see’
Higher order harmonics will depend on the ratio of the carrier wave frequency and the modulation wave frequency
PWM Duty Cycle
for full amplitude modulation
PWM Duty Cycle
for 50% amplitude modulation
modulation wave
carrier wave

## Slide 11: Power quality and harmonic analysis Switching strategies – Pulse-Width Modulation (PWM)
Apwm
Bpwm
Cpwm

## Slide 12: Power quality and harmonic analysis Switching strategies – Space Vector Modulation (SVM)
The aim of SVM is to approximate the reference voltage vector instantaneously by combining the switching states corresponding to eight basic vectors
A
B
C
0
0
0
0
1
0
0
1
1
1
0
2
0
1
1
4
1
0
1
6
0
1
0
3
0
0
1
5
1
1
1
7
1
0
,7
2
3
4
6
5
Notes: Space vector modulation (SVM) is to approximate the reference voltage vector () instantaneously by combining the switching states corresponding to the basic space vectors.
There are totally 8 space vectors corresponding to 8 different switching state combinations. The equation to get the voltage vector from 3-phase voltages is given by
, where
For every PWM period (switching period), the reference voltage vector is averaged by using its two adjacent space vectors ( e.g., Vector 1 and Vector 2 in the figure) for a certain duration of time and zero vectors (Vector 7 and Vector 8) for the rest of the period.
The advantage of SVM is that it has better utilization of DC-link voltage than that of SPWM.
1). For the same application, the DC-link voltage for SVM is lower than that for SPWM, then the IGBT devices with lower voltage ratings can be selected. Also the switching loss is lower than that of SPWM.
2). For the same DC-link voltage, the max. output fundament voltage by using SVM is higher than that of SPWM.
Exercise: Use SVM to control the 3-phase full-bridge inverter.
This example is also related to the model 'InductionMachineStartup.slx' in Chapter 2.
Open ‘IGBT_inv_3_svm_qd.slx’
Figure out how much DC-link voltage is large enough to generate the required output 3-phase voltages if SVM is used. In the model 'InductionMachineStartup.slx', the max. required fundamental voltage (phase-to-neutral, peak) is 377 V.
Complete the missing part in the model to get the modulation signals. A reference frame transformation block is necessary.
Solution file:
IGBT_inv_3_svm_qd_sln.slx
Space vector modulation (SVM) is to approximate the reference voltage vector (𝑣 ̅) instantaneously by combining the switching states corresponding to the basic space vectors.
There are totally 8 space vectors corresponding to 8 different switching state combinations. The equation to get the voltage vector from 3-phase voltages is given by
𝑣 ̅=2/3∙(𝑣_𝐴+〖𝑎∙𝑣〗_𝐵+𝑎^2∙𝑣_𝐶 ), where 𝑎=𝑒^(𝑗〖120〗^° )
For every PWM period (switching period), the reference voltage vector 𝑣 ̅ is averaged by using its two adjacent space vectors ( e.g., Vector 1 and Vector 2 in the figure) for a certain duration of time and zero vectors (Vector 7 and Vector 8) for the rest of the period.
The advantage of SVM is that it has better utilization of DC-link voltage than that of SPWM.
1). For the same application, the DC-link voltage for SVM is lower than that for SPWM, then the IGBT devices with lower voltage ratings can be selected. Also the switching loss is lower than that of SPWM.
2). For the same DC-link voltage, the max. output fundament voltage by using SVM is higher than that of SPWM.
Exercise: Use SVM to control the 3-phase full-bridge inverter.
This example is also related to the model 'InductionMachineStartup.slx' in Chapter 2.
Open ‘IGBT_inv_3_svm_qd.slx’
Figure out how much DC-link voltage is large enough to generate the required output 3-phase voltages if SVM is used. In the model 'InductionMachineStartup.slx', the max. required fundamental voltage (phase-to-neutral, peak) is 377 V.
Complete the missing part in the model to get the modulation signals. A reference frame transformation block is necessary.
Solution file:
IGBT_inv_3_svm_qd_sln.slx

## Slide 13: Power quality and harmonic analysis Comparing switching strategies
>> pmsm_detailed_drive
Outer loop: speed control
Inner loop: current/torque control

## Slide 14: Control design and linearization Detailed and average transistor bridges
>> igbt_power_inverter_det
1
Switch the inverter bridge to an average voltage model and comment through the PWM signal generator

## Slide 15: Control design and linearization Detailed and average transistor bridges
>> igbt_power_inverter_avg
2
Adjust the simulation mode and sampling rates appropriately
Notice that the controller runs at a 10 kHz rate

## Slide 16: Control design and linearization Detailed and average transistor bridges
>> igbt_power_inverter_avg
3
Open the PID tuner app from the Vd controller and re-linearize the closed loop based on the model at a simulation snapshot of 0.2 seconds

## Slide 17: Control design and linearization Detailed and average transistor bridges
>> igbt_power_inverter_avg
4
Use the sliders in the app to tune the Vd controller for the following performance targets:
bandwidth > 200 Hz
settling time < 5 milliseconds
overshoot < 5%

## Slide 18: Control design and linearization Detailed and average transistor bridges
>> igbt_power_inverter_avg
5
Click Update Block and verify the performance of the controller against the detailed switching inverter model in simulation
For simplicity, we will use the same newly computed PI gains for the Vq controller

## Slide 19: Control design and linearization Detailed and average transistor bridges
>> igbt_power_inverter
6
Combine both versions of the inverter in a single model using a Variant Subsystem
Subsystem & Model Reference  Convert Subsystem to…

## Slide 20: Control design and linearization Using subsystem variants
>> pv_mppt_inverter
Use the Variant Manager to set multiple variant configurations for simulation and testing
Variant  Open in Variant Manager

## Slide 21: Control design and linearization Initialization and trimming
>> mosfetbuckboost_avg
1
Use the Trim model option in the Linear Analysis tool
Analysis  Control Design  Linear Analysis…
2
Check the Specifications for the output voltages as known and trim the model
Change optimization method to nonlinear least squares

## Slide 22: Control design and linearization Initialization and trimming
>> mosfetbuckboost_avg
3
Verify trimmed operating condition and initialize model
4
Run simulation with the computed operating condition object as initial states

## Slide 23: Control design and linearization Plant identification from simulation data
>> sps_powersupply_sid
1
Use the Identify New Plant option in the PID tuner

## Slide 24: Control design and linearization Plant identification from simulation data
2
Choose Simulate Data to obtain I/O results from the simulation model
3
Set up a Step Response test with the following characteristics:
Sample Time = 5e-6
Offset = 0.5
Onset Lag = 0.003
Amplitude = 0.4
>> sps_powersupply_sid

## Slide 25: Control design and linearization Plant identification from simulation data
4
Run the simulation to obtain the identification data
5
Select the model structure and use the interactive handles to match the model to the data
>> sps_powersupply_sid

## Slide 26: Control design and linearization Frequency response estimation
>> mosfetbuck_fre
Open the Frequency Response Estimation tool
Analysis  Control Design  Frequency…
1
2
Create a new input Fixed Sample Time Sinestream with Ts = 1e-7
Use the pre-computed analytic transfer function of the converter GDBuck as a reference for selecting the test frequencies and increase the amplitude of the test sine waves to 1e-1

## Slide 27: Control design and linearization Frequency response estimation
>> mosfetbuck_fre
3
Check the Diagnostic Viewer option and run the estimation

## Slide 28: Control design and linearization Multi-input, multi-output control tuning
>> speedcontrol_dcmotor
From the model, open the Control System Tuner application
Analysis  Control Design  Control System Tuner…
1

## Slide 29: Control design and linearization Multi-input, multi-output control tuning
>> speedcontrol_dcmotor
2
In the Control System tab, capture a new operating point by taking a simulation snapshot at 10 seconds
3
In the Tuning tab, select the controller blocks to be tuned
4
In the Tuning tab, select the two new desired tuning goals
Goal #2: Target shape for open loop response
Response at current measurement
Open loop at the speed measurement
Crossover frequency = 100*2*pi rad/s
Goal #1: Desired step response
Input: speed reference
Output: speed measurement
Time constant = 0.05 seconds

## Slide 30: Control design and linearization Multi-input, multi-output control tuning
>> speedcontrol_dcmotor
5
Tune the system and check that both requirements are being adequately satisfied after the optimization
6
In the Control System tab, select Update Blocks and verify the performance of the controller against the nonlinear model in simulation